## Slide 1: The power supply system of the basic facility NICA

## Slide 2: The basic facility NICA
The power supply system of the output channel beam from the Nuclotron
design, fabrication
The power supply system of the channel beam in
bld. 205,BM@N
design, fabrication
The power supply system of the Collider
design, fabrication
The power supply system Booster
design, fabrication
The power supply system of the Nuclotron
modernization
Notes: Системы питания NICA:
сверхпроводящего быстроциклирующего синхротрона Бустера, статус – проектирование, создание
сверхпроводящего быстроциклирующего синхротрона Нуклотрона, статус – модернизация,
сверхпроводящего коллайдера, статус – проектирование,
«теплых» магнитных элементов каналов транспортировки заряженных частиц, статус – коренная модернизация

## Slide 3: The specifics of the power supply systems superconducting structural magnets of the synchrotrons and Collider
For modern accelerator complexes require precision system MW power supply, the stability of currents of consumers should be 0,001%-0,01%.
Superconducting magnets when fast cycle current requires the maximum dynamic range of the voltage – the highest value at the factory current and almost zero on the "plateau" of the current (c di/dt=0), while the output current of the magnets, the stored energy should be and often are recovered in the network.
Providing at a predetermined level of stability required, managed in a cycle of the ratio of the field/(field gradient) in all families of structural elements of the magnetic – dipole, focusing and defocusing quadrupole magnets.
Power system must have a subsystem of an emergency evacuation of energy from SC-magnets with the loss of the superconducting state in them.

## Slide 4: The power supply system of the Nuclotron
parameter | value | 
inductance of the dipole magnets, Lm | mH | 100
inductance of the quadrupole focusing magnets, Lf | mH | 10
inductance of the quadrupole defocusing magnets, Ld | mH | 10
Maximum current dipole, focusing and defocusing magnets, Im, If, Id | кА | 5,89
Relative current stability, ∆Im/ Im |  | 2*10-4
The range of changing the current of focusing magnet, % от If | % | 10
The range of changing the current of focusing magnet, % от Id | % | 10
The maximum voltage applied to a circuit successively included all structural magnets at a rate of change of the magnetic field of 1,0 (0,6) T/s, Uи | В | 360 (216)
System requirements power:
- formation of magnetic fields of desired magnitude for a given rate of growth of the field with energy recovery in the decline field in accordance with the desired cycle,
ensuring the defined accuracies and ranges of change of the currents in the magnetic structural elements of the Nuclotron, - ensuring trouble-free operation of superconducting magnets in case of a normal zone.
Notes: Цикл переделать

## Slide 5
Power system structural magnets of the Nuclotron
общий вид

## Slide 6
LEM, current sensor ITZ FLEX ULTRASTAB: measuring head and electronics module
Control panel build.1A - front measuring apparatus
The subsystem for precision measurement of currents of the Nuclotron
Main characteristics ITZ FLEX ULTRASTAB 10kA:
Nominal current measurement: 10000 ADC
Excellent linearity, from 1 to 10 ppm
High resolution Initial offset: < 2 ppm
Very low offset drift: from 0.1 to 0.6 ppm/K
Overall accuracy @ IPN @ +25°C: between < +/- 3 ppm and < 12 ppm
Wide frequency bandwidth from DC up to 500 kHz (+/- 3 dB)
ZETLAB, module ZET220
Main characteristics:
frequency: up to 8 kHz
Analog output (DAC): 16 bits
Analog input (ADC): 24 bit total conversion
The total conversion rate of 200 kHz

## Slide 7
I19 =3253,58А
I37 = 32,73А
the ratio of I37/I19
0,0005
82,15А
0,75А
injection
the ratio of I19/I37
0,0005
I plateau = 32,74А
I rms ac = 0,07А
& I = 1,2*10-4
I plateau = 3253,58А
I rms ac = 0,14А
& I = 2,4*10-5
The subsystem for precision measurement of currents of the Nuclotron
made upgrade regulators 19,20 TV and 37ТV
In the 54th session of the Nuclotron received the repeatability of the magnetic field at injection level 10-5

## Slide 8: The power supply system Booster

## Slide 9: Stand testing prototype power supply Booster
Bld. 1A
Power supply PS600-80D
600A x 80V
EVPU, Slovakia
Power supply ИП600-80Д
600A x 80V
НПП ЛМ Инвертор, Россия

## Slide 10
The choice of the structure of the power supply Booster
"+" circuit with the energy storage(ES) Converter:
lack of components of the network harmonics in the surge current to the load,
simplifying energy recovery: not required powerful rectifier with a complicated control system for transfer of power to the grid,
unloading of the network infrastructure (2,8MWt)
"-" schema the ES:
-ES considerable stored energy (potential "bomb"), as a consequence of the characteristics and the additional costs of service
- ES complex, compound device, it is necessary to control the current loading, temperature and other parameters in each Assembly, to provide for the possibility of switching and rapid discharge of the storage if necessary.
Manufacturer of power supply
НПП ЛМ ИНВЕРТОР (ВЭИ, Россия)
Notes: -Структура современного источника питания, работающего в циклическом режиме, приведена на верхнем рисунке.
-Разделительный трансформатор понижает входное напряжение до требуемого уровня. Далее включается 6-ти фазный управляемый мост. Меняя алгоритмы управления транзисторами моста, можно организовать передачу энергии как от сети к конденсаторному накопителю, так и обратно.
-Энергия от конденсаторного накопителя подается в DC/DC преобразователь и через LC-фильтр поступает в нагрузку.
-Регулирование требуемого параметра в нагрузке осуществляется за счет длительности открытия ключей по технологии ШИМ. Рабочая частота выходного моста, как правило, единицы-десятки кГц. Это определяет относительно небольшие габариты LC-фильтра. DC/DC преобразователь также способен передавать энергию от конденсаторного накопителя в нагрузку и рекуперировать ее из нагрузки в накопитель.
-Мощность, подаваемая в нагрузку, проходит через все составные части источника и определяет габариты и вес всех устройств, в том числе и потери в них. Высоковольтные энергетические сети Лаборатории должны обеспечить пропускание требуемых потоков энергии. При этом происходит ухудшение для других потребителей качества энергоснабжения из-за внесения источниками высших гармоник в сети 50Гц, просадок/всплесков амплитуд напряжения и т.д.
Структурная схема источника на суперконденсаторах в целом очень похожа.
Главное же отличие состоит в том, что здесь трансформатор и выпрямитель не используются с целью организации закачки и рекуперации энергии из сети в нагрузку. В классическом источнике конденсаторный накопитель является только буферным элементом между выпрямителем и преобразователем, в то время как в рассматриваемой схеме накопитель имеет первостепенное значение. DCDC передает энергию из накопителя в нагрузку, а потом возвращает ее обратно же в Накопитель. Необходимо только предварительно зарядить накопитель, а для этого не требуется такой мощный и сложный выпрямитель.

## Slide 11: Subsystem evacuate energy
Plot the potential distribution of the magnets of the Booster during the evacuation current is 10kA .
The main provisions of the system of evacuation:
time constant of the energy output 160мс,
potential relative to the ground on the SC magnet is not more than 500V,
the reliability of the system.
Model EES
Prototype EES

## Slide 12: The concept of structural magnets power Booster
0,69kV
The layout of the power system
SFT
Test load
Power switch
SEE
MM BOOSTER
BOOSTER
PS1
PS2, PS3

## Slide 13
1 | Number of power supplies | 2
2 | Maximum power | 600 kW
3 | Maximum voltage | 55 V
4 | Maximum current | 11 kA
5 | Inductance | 45 mH –regime 1 1-10 mH-regime 2
7 | Relative current stability at di/dt ≠0 and magnetic field rate 0.1 T/s | 2*10-4
8 | Pulse duration at increase of magnetic field | 18 s
9 | Relative current stability at di/dt=0. | 10-5
10 | Maximum pulse duration at di/dt=0. | 24 h
11 | Pulsation of output voltage at di/dt ≠0 | At max current it is less 300 mV At min current it is less 100 mV
13 | Dynamic current diapason | 30…100% from Iмакс
14 | Stability to short circuit | Yes
15 | Work regime | - static - dynamic at di/dt ≠0…+/-0.56 kA/s
Schematic diagram
The cycle of the magnetic field of the Collider
The power supply system of the Collider
Принципиально-монтажная схема

## Slide 14: Evacuation energy switch collader
The main parameters:
Static mode of operation
Minimization of energy losses
The reliability of the detection of the breakdown of superconductivity
Parameters ВАБ49-6300:
nominal current - 6300А
nominal voltage - 1050V
off time - 8ms
reliability of shutdown
Kinematics ВАБ49
Общий вид
Prototype EES
Model EES

## Slide 15
The power supply system of the channel beam in bld. 205, BM@N, NICA
BM@N
Bld.205

## Slide 16
The structure of the power supply system of the magnetic elements
Параметры магнитных элементов
Группировка по току/напряжению источников магнитных элементов
Required:
upgrade 2 switchgear 6kV network,
to create a distribution subsystems 3-phase network 0,69 kV
create 35 high-current precision power supplies
to create a subsystem for back-up power loads on the grid constant current,
to create a subsystem load switching in power circuits,
to create a subsystem for control and monitoring all.

## Slide 17
working documentation
electric principled scheme
The power supply system of the output channel beam from Nuclotron Bld. 1B
working documentation
placement plan

## Slide 18
SG-0,69кV
SG-6кV
SB-0,4кV
power supply
power switch
power supply 2
control room
Bld. 1B
Commissioning in late 2018
The power supply system of the output channel beam from Nuclotron Bld. 1B

## Slide 19
The power supply system of the channel beam in bld. 205, BM@N
Power supply КВТМС, bld. 208
bld. 208
bld. 205
Existing power system :
- Switchgear SG-6kV 64 cells with oil circuit breakers,
- 25 (19) power supply , type «КВТМС» 130V x 3500А,
- 20 power supply , type «ТВ», 230V х 1600А,
- 10 power supply , type «ТВ», 230V х 600A,
Total 55 unit power supply,
- Installed capacity 20МВА
SG-6kV
Power supply TB
Power switch «КВТМС»»

## Slide 20
The power supply system of the channel beam in bld. 205, BM@N
electric principled scheme

## Slide 21
The power supply system of the channel beam in bld. 205, BM@N
The placement of the power sources in technological areas, bld. 205
Bld. 205b experimental hall
Bld. 205
The road
The road
Bld. 205
The placement of the power sources external bld. 205, new bld.
New bld.
New bld.
Bld. 205
The road
The road

## Slide 22
ИП600-180 ЛМ Инвертор
Creating power source ИП300-8, 300A x 8V
Creating power source system
Active filter АФВТ 600-25
ЛМ Инвертор
remote control ИП300-8 and ИП600-180
Switchgear ПС13, bld.1A

## Slide 23: Thank you for your attention!