## Slide 1
GRID2018
NRC KI – ITEP
I.Korolko, V.Kolosov, M.Prokudin
Experience with ITEP-FRRC
HPC facility

## Slide 2
FAIR-Russia supercomputer project
Project was suggested by GSI and ITEP scientists and
supported in 2011-2014
by ROSATOM corporation and Helmholtz association.
(85% ROSATOM + 15% Helmholtz + green cooling)
The main aim was to build 10K cores facility
Which was done in 4 years and about 130M roubles
Container, cooling system (green technology) came from GSI

## Slide 3
Aims for FAIR-Russia supercomputer
Optimization of FAIR detectors (CBM, Panda and others)
Development of reconstruction algorithms for FAIR
Lattice QCD calculations (former M.Polikarpov laboratory)
CBM experiment - study of “cold” and dense barionic matter
up to 10 MHz event rate (T0 is not known – 4D reconstruction)
up to 1500 secondary particles per Au+Au central collision
No hardware trigger system – need to analyze all events

## Slide 4
2011 – commissioning of 1st stage
1st stage was mounted in ITEP computer center in December 2011
2560 CPU cores (16 cores AMD) – intensively used by first users

## Slide 5
2011-2012 preparation of facility site
2011-2012 preparation of place for container and cooler

## Slide 6
2012 – delivery of container and cooler
October 2012 – container and cooler were delivered and installed in ITEP

## Slide 7
2013 – container and cooling are ready

## Slide 8
Green Cube at GSI (February 2016)
Green container in ITEP is a small brother of Green Cube at GSI

## Slide 9
Effective (green) water cooling
Hot water is collected from passive rear doors and then is pumped to the street cooler

## Slide 10
Effective (green) water cooling
JAEGGI cooler with massive copper heat exchanger which is irrigated with water
during hot summer period (need to decrease water hardness – special water station)
Poplar blossom is a headache…

## Slide 11
Cooling efficiency
One year time interval: September 2017 – September 2018
Below 30 degrees (at the entrance of computer boxes), but bin size is too rough

## Slide 12
Cooling efficiency
3 summer months: June 2018 – August 2018 ~10% of electricity is spent for cooling
We would add chiller for reliability and safety…. (and special roof from the direct sun)

## Slide 13
Computing hardware
CPU: 16 x 20 x 2 x AMD 6272 16 cores x 2.1 GHz (10240 cores)
  2 Gb RAM per core
GPU: 40 x Nvidia Kepler K20X (8 servers)
Mass storage system:
  1080 Tb lustre distributed filesystem
CPU power: 58 TFlops
GPU power: 40 TFlops
Peak power consumption: 180 kW
  Cooling power: 18 kW
Online: 98% (last 3 years)
  3 stops, each about a week due to cooling maintenance
System load: more than 90%

## Slide 14
System load
One year time interval: September 2017 – September 2018
Almost all the time system is full
Users (Lattice QCD) prefer to have more memory – up to 16 GB per job
(last year we have switched off 25% of CPUs to save electricity)

## Slide 15
Lessons we have learnt
1. NEVER believe in advertising hype – try to test hardware yourself (16 cores = 8 pairs)
2. Three year warranty looks OK (10 broken blades were found after 2 years already)
3. Today quality decreases while the prices go up (fans in power supplies)
try to buy 20-30% reserve power supplies and fans for them
4. In 2011 2 GB per core looked OK, today it is not enough
modern 32 core processors – do we really need them… (lattice QCD needs)
5. Special servers for data analysis (need more experience)
6. Green cooling technology is OK but for small systems we would add 2 things:
- roof from the sun (up to 10 kW additional heating)
- chiller for hottest summer time (2 months)
7. Think about possibility of future upgrade from the first days of project (we did)

## Slide 16
Ready for upgrade
It is time to upgrade the hardware of ITEP facility.
About 30% of hardware could be reused (Infiniband, network equipment, racks)
We need to buy new blades and file servers only
For the same electricity we can increase:
- CPU power by a factor of 5-6
- capacity of mass storage system by a factor of 5