## Slide 1: MPD cooling system proposal
V. Benda

## Slide 2: MPD shield cooling by GHe/LHe or by GN2/LN2? - at nominal
Magnet
  Thermal loads of MPD magnet P=82W @ 4.5K reference: 3НМ1002.00.000ТО , table 2.4.3.3.1, page 28
  Current leads PCL=10W reference: 3НМ1002.00.000ТО , table 2.4.3.3.1, page 28
  Cooling power of Satellite PS=100W @ 4.5K reference: ILK-B-1-16-319a_v
  Whole cooling power of the Satellite is required by MPD magnet
Shield
  Thermal load of MPD thermal shield Q=2200W @ 80K reference: 3НМ1002.00.000ТО , table 2.4.3.3.1, page 28
    If T1=300K and T2=80K
  Thermal load of MPD thermal shield Q=3000W @ 30K estimation
    If T1=300K and T2=43K, T2= Tin(5K)+Tout(80K)/2=42.5K, dT=75K
  Required flow of LHe
    m=Q/(Cp x dT)=3000/(5200 x 75)=0.008kg/s=8g/s ~ 160W
    In case of using LHe for MPD thermal shield cooling extra 160W from the Satellite is required. This extra power is not available.
This analysis is done for the normal operation @ 4.5K
For cool down of the system, higher cooling power is required
Conclusion
  Original proposal of using GN2/LN2 for cool down/warm up and normal operation is better adopted solution
    From thermodynamic point of view better and more economic solution (in long term)
    No new questions which could delay the project will be raised. The “LHe” solution would have to be discussed and approved by ASG

## Slide 3: MPD satellite, no space on the top plate Modification is difficult, warranty would be lost

## Slide 4: Схема предварительной подачи LN2
LN2
GN2
Испаритель 5kW
MPD magnet
Экран
MPD control cryostat
Satellite
Гибкая криогенная линия
Стена
LN2 tanks
Cold GN2
Heater 5kW
MFS
From CERN
LN2 filling
By-pass for LN2 to be added
To be used for shielding of LHe line #1

## Slide 5: MFS - magnet flushing station, with Unicos control system For time being not in use at CERN

## Slide 6: Provisional solution
LHe line #1

## Slide 7: Location for LN2 and LHe tanks – waiting for approval

## Slide 8: Схема предварительной и окончательной подачи LN2
LN2
GN2 warm
Испаритель
Нагреватель (Смесительная камера)
GN2 cold
(HP GN2 warm)
MPD magnet
Экран
MPD distribution box
Satellite
Ожижитель
Гибкая криогенная линия
Стена
LN2 tanks
LN2 filling

## Slide 9: Final LN2 pre-cooling box
To be analyzed if this part is necessary

## Slide 10: Окончательное решение, if required the provisional LHe solution can stay in place

## Slide 11: Small liquefier
MPD requirement
Nominal: 4.34g/s = 129l/h @ 4.5 K
Cool down/Warm up: 16.2 g/s of GHe T=80K – 5K
From this point LHe is required, but how much?

## Slide 12: Simplified estimation of required liquefier cooling power for magnet cool down
Cool down by satellite
  From 300K down to 80K indirectly by LN2
  From 80K down to 5K by LHe considering that all helium enthalpy is used by means of satellite heat exchanger
    In this case for cool down of Aluminum from 80K down to 5K is required 0.2l(LHe)/kg(Al)
    For 14t of magnet 336 kg of LHe is required
    If we consider cooling speed 1K/h, the required flow of LHe is m=1.2g/s
    It can be expected that cooling speed below 80K can be much higher (no shrinkage)
      In this case with Linde liquefier L280 of cooling power 10g/s of LHe, the cooling speed of the magnet would be nearly 10K/h which is fully satisfactory