## Slide 1: Status of MPD infrastructure focused on cryogenics
V. Benda

## Slide 2: MPD P&I, Process and Instrumentation diagram
Final infrastructure for cool down to 4.5 K by LHe
Solenoid
Control cryostat
Refrigerator
GHe heater
GN2 heater
MFS
LHe tank
LHe tank
LN2 tank
LN2 tank
LHe line
LN2 line
Purge pump
Compressed air for valve actuators
Names of interfaces

## Slide 3: MPD – Infrastructure and their key components
LN2 tanks (2): Chart-Ferox started production on April 2021. Required: foundation, including the road, roof, lighting etc.
LHe line: A.S.Scientific UK will start the production on April 2021
MFS arrived from CERN to JINR b. 203A on 19 March
  In process of restoration: test, ordering of missing elements, control system
GHe & GN2 heater: Heating cartridge-waiting for final quotation. Technical Specification for the envelop in progress
LHe tanks (2) to be borrow from Gelimash. Required: foundation, roof, lighting etc.
Vacuum pump: Technical Specification in progress
Lines: see the next slide
ILK (D) – Refrigerator and Control cryostat future collaboration
  Spare parts
  Assembly of the Satellite refrigerator & modification
  Dummy in negotiation
  Control system (PLC automat) - discussion
ASG (It) – Solenoid. ASG experts arrived on Monday 19 April for 3 days
  Opening of the MPD magnet transport box – done.
  Visual and electrical test – done
  Preparation for next visit – pumping & leak test
MPD Control system (PLC)
  P&I is ready
  List of instrumentation and nomenclatures is in process, see next slides
  Function Specification to be done
  Hardware to be defined and ordered. Software to be written
Document server – highest priority, in trial operation
Chimney of solenoid
2021-3-23
Solenoid
Heating cartridge

## Slide 4: Cold and warm pipes required
Interfaces are defined in P&I diagram

## Slide 5: List of Instrumentation, example from other project as illustration & MPD draft
№ п.п. | Обозначение на схеме | Наименование | Принадлежность | Среда | Параметры |  |  |  |  |  |  |  | Описание |  | Сигнал | Подрядчик
 |  |  |  |  | Температура, К |  |  |  |  |  |  |  |  |  |  | 
 |  |  |  |  | Рабочая температура, К | min | max | РN, bar | Давление на входе, bar | Давление на выходе, bar | DN | Kv | ТИП ПРИВОДА | Тип |  | 
48 | V-2 | on/off valve | CONTROL CRYOSTAT | N2 L/G (GN2) |  | 77,15 | 313,15 | 25 |  |  | 15 |  | Пневматический мембранный привод (vonRohr) | МА16А6-162mm | PROFIBUS PA | weka
49 | V-3 | control valve | CONTROL CRYOSTAT | N2 L/G (GN2) |  | 77,15 | 313,15 | 25 |  |  | 8 |  | Пневматический мембранный привод (vonRohr) | МА16А6-162mm | PROFIBUS PA | weka
50 | V-4 | control valve | CONTROL CRYOSTAT | Helium L/G GN2 |  | 4,15 | 313,15 | 25 |  |  | 25 |  | Пневматический мембранный привод (vonRohr) | МА16А6-162mm |  | weka
51 | V-5 | control valve | CONTROL CRYOSTAT | Helium L/G GN2 |  | 4,15 | 313,15 | 25 |  |  | 10 |  | Пневматический мембранный привод (vonRohr) | МА16А6-162mm | PROFIBUS PA | weka
52 | V-6 | control valve | CONTROL CRYOSTAT | Helium L/G GN2 |  | 4,15 | 313,15 | 25 |  |  | 10 |  | Пневматический мембранный привод (vonRohr) | МА16А6-162mm | PROFIBUS PA | weka
53 | V-7 | control valve | CONTROL CRYOSTAT | Helium L/G GN2 |  | 4,15 | 313,15 | 25 |  |  | 20 |  | Пневматический мембранный привод (vonRohr) | МА16А6-162mm | PROFIBUS PA | weka
54 | V-8 | control valve | CONTROL CRYOSTAT | Helium L/G GN2 |  | 4,15 | 313,15 | 25 |  |  | 40 |  | Пневматический мембранный привод (vonRohr) | МА16А6-162mm | PROFIBUS PA | weka
55 | V-9 | control valve | CONTROL CRYOSTAT | Helium L/G (GN2) |  | 300 | 313,15 | 25 |  |  | 6 |  | Пневматический мембранный привод (vonRohr) | МА16А6-162mm | PROFIBUS PA | weka
56 | V-10 | control valve | CONTROL CRYOSTAT | Helium L/G (GN2) |  | 300 | 313,15 | 25 |  |  | 6 |  | Пневматический мембранный привод (vonRohr) | МА16А6-162mm | PROFIBUS PA | weka
57 | V-11 | safety valve | CONTROL CRYOSTAT | GN2 |  |  |  | 2,5 |  |  |  |  |  |  |  | 
58 | V-14 | vacuum break valve | CONTROL CRYOSTAT | GN2 |  |  |  |  |  |  | 200 |  |  |  |  | 
59 | V-16 | safety valve | CONTROL CRYOSTAT | GN2 |  |  |  | 0,6 |  |  |  |  |  |  |  | 
Draft of MPD List of Instrumentation

## Slide 6: Sensor naming - Nomenclature to be done sample from CERN system…

## Slide 7: Layout

## Slide 8: MPD magnet cool-down to 80K by LN2
  To increase the speed of work on the MPD project, cooling to 80 K is being prepared
  At 80K, most of the possible problems will appear
    Cold leak and electrical short circuit coil to ground
  This cooling will demonstrate the progress of the project
  In the event of the magnet malfunction, there will be enough time to repair it
  For this purpose, the MFS (Magnet Flushing Station), which was used at CERN for a similar task was brought and it is under preparation
Slow magnet cool-down at CERN
LN2 storage container
Test cryostat
MFS
PLC control system

## Slide 9: MPD solenoid cool-down to 80K at JINR, MFS preparation
Existing valve
LN2 distribution in b.203A
Preparation and testing in b.203A
MFS

## Slide 10: MPD solenoid cool-down to 80K
Draft of Technical Specification for the transient parts is ready
Control cryostat

## Slide 11
Thank you for your attention