## Slide 1
V.Karpinskii on behalf of the team
Power supply system for magnetic elements of transport channel for particle beam of the Accelerator complex
BM@N, NICA

## Slide 2
Hall 205
Bld. 1
Accelerator complex,
beam transport channels
Power supply system for magnetic elements of transport channel for particle beam of the Accelerator complex, BM@N NICA
beam output channel from the Nuclotron
beam channel hall 205
November 2021
V.Karpinskii

## Slide 3
Power supply КВТМС, bld. 208
bld. 208
bld. 205
The old power system includes:
- SG15 substation with 64 cells with oil switch, 6 kV network,
25 power supplies, type «КВТМС" 130V x 3500A,
20 power supplies, type «ТВ", 230V x 1600A,
10 power supplies, type «КВ", 230V x 600A,
A total of 55 units of sources + associated equipment. The installed capacity is 20 MVA.
Accommodation in 3 floors of the addition building 205 and all bld. 208.
Power supply TB
Power supply system for magnetic elements of transport channel for particle beam of the Accelerator complex, BM@N NICA
SG15
power switchboard
November 2021
V.Karpinskii

## Slide 4
output channel beam from N
channel beam hall 205
Necessary:
- modernization of 2 substations SG-K and SG15,
- to make a distribution and reservation subsystem over a 0.69 kV network,
- to produce 43 precision current sources,
- to make a DC reservation subsystem,
- to create a subsystem for managing and controlling the all complex.
Block diagram of power supply system
Power supply system for magnetic elements of transport channel for particle beam of the Accelerator complex, BM@N NICA
November 2021
V.Karpinskii
Notes: individually

## Slide 5
Power supply system of output channel of beam from the Nuclotron
Power supply
scheme
Placement,
bld.1B
Power supply convertor
4000A, 150V,
stability of the current – 100ppm
Power supply system for magnetic elements of transport channel for particle beam of the Accelerator complex, BM@N NICA
November 2021
V.Karpinskii

## Slide 6
SG-0.4кV
Power supply
Power switches
Power supply for application channels
Control room
bld. 1B
SG-0.69кV
SG-K
Power supply system for magnetic elements of transport channel for particle beam of the Accelerator complex, BM@N NICA
Power supply system of output channel of beam from the Nuclotron
November 2021
V.Karpinskii

## Slide 7
SG-K, nets 6kV
SG-0.69кV
Power switches
Power supply
the main equipment was installed in 2020
Now, work is in progress to install cable lines from power sources to magnets.
The total length is more than 6 km
Power supply system for magnetic elements of transport channel for particle beam of the Accelerator complex, BM@N NICA
Power supply system of output channel of beam from the Nuclotron
November 2021
V.Karpinskii
Notes: Основное оборудование смонтированно в 2020 году the main equipment was installed in 2020
пуско наладка commissioning

## Slide 8
Placement,
bld.208, 205
Hall 205
Bld.1
beam transportation line
Bld. 208
Power supply system of transport channels of beam hall 205
Power supply scheme
Modular bld. substation SG15
Equipment PSS
Modular bld. Transformers
Power supply system for magnetic elements of transport channel for particle beam of the Accelerator complex, BM@N NICA
November 2021
V.Karpinskii

## Slide 9
Equipment PSS
Equipment PSS
Magnets of chanels
Magnets of channels
Location of the equipment PSS
Modular bld. substation SG15
Modular bld. Transformers
bld.205
Power supply system for magnetic elements of transport channel for particle beam of the Accelerator complex, BM@N NICA
November 2021
V.Karpinskii

## Slide 10
Power supply scheme SG15, 8MW
Develop of substation SG15
Main equipment
1. Modular bld. (lxwxh) 25x5.4x4.5 m
2. Busbar 2 sect., 2kA
3. Vacuum sw. BB/TEL 24 pieces 6 kV, 1-2kA
Plan modular building SG15
25m
5,4m
November 2021
V.Karpinskii

## Slide 11
Develop of substation SG15 and Transformators
Equipment of substation SG15 and Transformer
Substation SG15,
HV cell D-12P classic
Relay protection equipment
Vacuum switch
BB/TEL 6 kV
Power Transformer 6/0.69 kV 1,6MW
November 2021
V.Karpinskii
Notes: Состав подстанций

## Slide 12
Bld. 208, august 2018
bld.208 , february 2020
Power supply system for magnetic elements of transport channel for particle beam of the Accelerator complex, BM@N NICA
November 2021
V.Karpinskii

## Slide 13
Mdl. bld. SG15 and Transf., autumn 2020
Power supply system for magnetic elements of transport channel for particle beam of the Accelerator complex, BM@N NICA
water cooling system
autumn 2021
November 2021
V.Karpinskii

## Slide 14
Power supply system for magnetic elements of transport channel for particle beam of the Accelerator complex, BM@N NICA
Room 111
autumn 2020
Room 108
autumn 2020
autumn 2021
autumn 2021
commissioning is underway
November 2021
V.Karpinskii

## Slide 15
Thank you for your attention!