## Slide 1: standards
Related to human factor

## Slide 2: REVIEW TEAM SELECTION
The number of people needed to conduct the control room design review cannot be precisely
defined . Both team size and team makeup can be expected to vary according to plant type, the
kind of control room , and control room/plant status. In general , it appears that a basic technical
team would include :
• A nuclear systems engineer
• An engineer/architect with control room design experience
• A senior reactor operator or operations technical advisor with operating experience
A human factors engineer

## Slide 3
Technical team direction and support will be needed . A project director should be assigned to
provide team management coordination , direct and support day-to -day team activities , arrange
for consultant/specialist support when needed , and direct the evaluation , implementation , and
reporting process . The project director should also be responsible for scheduling and controlling
all activities within the control room , including assignment and involvement of operators to assist
the review team .
Administrative and documentation support should also be planned for and made available to
the technical team and project director . Principal tasks other than typical administrative support
tasks would involve the acquisition and maintenance of reference materials , management of review
team documents (e.g. , control room survey and measurement reports ) , and control of special
documentation systems such as photographic documentation .

## Slide 4: Scheduling
Review team activities within the control room should be scheduled to minimize interference with control room operations, particularly with respect to operating plants . Accurate control room mockups or simulators may be used to accomplish some of the review tasks , and others may be accomplished during plant shutdown periods . However, some tasks ( e.g. , measurement of ambient conditions such as noise levels ) need to be carried out in the control room during plant operation in order to establish accurate data .
The schedule should extend from the planning phase through preparation of the control room design review report . The responsibilities and functions of individual team members should be assigned at this time, and team member activities should be integrated into the overall review assessment, and implementation schedules.

## Slide 5: REVIEW PROCESSES
Six processes are recommended to establish for identifying human
engineering discrepancies of both completeness and human engineering suitability:
1. A review of operating experience
2. A review of system functions and an analysis of the tasks involved in control room
operator functions.
3. An inventory of control room instrumentation and equipment.
4. A survey of the human engineering acceptability of control room components and
environmental conditions such as lighting , noise/sound control , etc.
5. Verification of task performance capabilities.
6. Validation of control room functions .

## Slide 6: Process 5
Verification of Task Performance Capabilities Control room components should also be examined with reference to requirements for specific , individual tasks . From this perspective there are two issues . First it is necessary to establish whether the instrumentation , controls, other equipment , and materials needed for each task are present in the control room . (A corollary concern is whether unnecessary items are present that may make the work space less efficient . ) The second issue is whether the present items fit their task uses. For example, if the operator must determine whether the margin for a parameter is being maintained , then do the displays provide sufficient resolution to achieve this task ? Do displays show the units of measure that must be applied or is conversion required ? Examination of panel layout and control -display integration also requires a task perspective.

## Slide 7: Staffing
The staff should include at least one systems analyst experienced in the study of complex systems .The experience of this individual should help to assure that major points , such as potential operator functions during emergencies
A control room operator who has a minimum of two years of operating experience should be included on the review staff. The experience of the operator should aid in the analysis of plant-specific items and help constrain the analysis to realistic control room problems . Additional experienced operators, technical advisors , engineering personnel , and others ( e.g. , training personnel , procedures developers) should be consulted as necessary to assure accurate and complete definition of control room operator task actions and the associated instrumentation , control , and equipment requirements .