## Slide 1: The model solenoid creation of the HTS magnetic energy storage SMES for SC magnets power supply system of NICA Booster and Nuclotron
I.I. Donguzov, O.M. Golubitsky, M.V. Ilin, D.N. Nikiforov, M.S. Novikov, A.A. Kotova,
M.V. Petrov, G.G. Khodzhibagiyan, A.V. Shemchuk

## Slide 2
2
SMES
Purposes:
Decreasing pulsations of superconducting magnets operating current
Reducing inductive load influence to the city’s power grid
Minimizing of energy consumption
Parameter | Meaning
Inner diameter | 400 mm
Outer diameter | 960 mm
Height | 900 mm
Number of layers | 14
Operating current | 6.7 kA
Inductance | 120 mH
Stored energy | 2.74 MJ
Operating temperature | 30 K
Refrigerant | Neon
SMES (Superconducting Magnetic Energy Storage)

## Slide 3
Purposes:
Testing technologies of production and assembling of such type HTSC solenoids.
Achieving the same proportions of mechanical deformations like at SMES
3
Model SMES
Parameter | Meaning
Inner diameter | 290 mm
Outer diameter | 459 mm
Height | 500 mm
Number of layers | 4
Operating current | 13 kA
Inductance | 1,79 mH
Stored energy | 163 kJ
Operating temperature | 4.5 – 50 K
Refrigerant | Helium
Model SMES
SMES vs Model SMES

## Slide 4
Parameter | Unit | Meaning
Conductive layer |  | ReBCO
The width of the conductor | mm | 4
The Thickness of the conductor | um | 100
Substrate material |  | Hastelloy C276
The thickness of the substrate | um | 100
Crit. current (77 K), | A | 100-150
Layer thickness Ag | um | 1-10
Layer thickness Cu | um | 0-100
ReBCO tape (rare-earth barium copper oxide tape)
3
Superconductor
Buffer layer
HTC
Ag
Cu
Hastelloy
The structure of the HTS tape
Tapes from different manufacturers

## Slide 5
Cu-Ni tube
Brass tape
HTSC tape (SuperOx)
Kapton tape
Fiberglass tape
HTSC cable SMES
Nuclotron type tubular cable – created in 1979 and first tested in 1980 at JINR
Cu-Ni tube
Strands of the superconductor
Ni-Cr wire
Kapton tape
Fiberglass tape
3
HTSC cable
Winding HTSC tapes on a tube
Cable machine
HTSC cable

## Slide 6
The assembly consistency of one section of the model solenoid
Half section of the model solenoid
Model SMES
4
The model solenoid design

## Slide 7
3D model of the HTSC cable connection
Voltage output circuit for the model solenoid
9
Electrical connection of the cable

## Slide 8
cRIO-9057
8
Quench detection system
ADC NI-9202
± 10В
ADC NI-9238
± 0.5В
Current sensor LEM ITZ - 16000
Energy evacuation switch
Current source
MOXA
PC
DAC NI-9263
± 10В
Current value
Energy evacuation signal
Layers
RS-485
Ethernet
Current leads, bridges
Model SMES

## Slide 9
9
Thermometry system
Measuring range: 4 - 300 K;
Accuracy: ± 0,3 % in the range up to 30 K;
Number of voltage measurement channels: 8;
ADC bit rate: 24 bits;
Built-in current source: 10, 100 мкА;
Supply +24 DC / PoE.
Measuring equipment
Current source +
Current source -
Chanel 1 +
Chanel 1 –
Chanel 2 +
Chanel 2 –
Chanel 8 +
Chanel 8 -
Connections of temperature sensors

## Slide 10
The location of strain gages and temperature sensors on the frame of the model SMES:
1 – temperature sensors, 2 – strain gages.
At a deformation of 1000 microns/m, a resistance change of 0.77 Ω at room temperature will follow
Operating temperature range - -269 - +250 ⁰С
Rated resistance - 350 Ω
The length of the measuring grid - 10 mm
The width of the measuring grid - 3.5 mm
9
Strain gauge system

## Slide 11
Conclusion
10
The design of the model solenoid has been developed, technical documentation has been prepared, parts are being manufactured.
A hardware and software complex based on NI equipment is being developed to determine the normal-conducting area in the HTSC cable.
A system for data acquisition on cryogenic parameters, voltages, and mechanical deformations of solenoid is being developed.
The production of the model solenoid is scheduled for autumn 2024.

## Slide 12: The model solenoid creation of the HTS magnetic energy storage SMES for SC magnets power supply system of NICA Booster and Nuclotron Ilya Donguzov, donguzov@jinr.ru
Thank you for your attention!

## Slide 13
900 mm
500 mm
960 mm
459mm