## Slide 1: Engineering infrastructure of the NICA complex
20 January 2025
JINR
Programme Advisory Committee for Particle Physics
61st meeting
Speaker: K. Mukhin

## Slide 2: Plan of talk
Construction of the collider building #17
Status of engineering systems
-water,
- power electricity,
- automatization of engineering systems for the NICA complex
Upgrading and status of liquid helium and nitrogen production
Status of MPD engineering system and cooling progress
Main power station GPP1
Site infrastructure development
- reconstruction of the entrance gate
- new parking area

## Slide 3: Collider building #17
Ground floor
First floor
Some data of building parameters | 
Total area of the building, m2 | 30 800
Covered area, m2 | 22150
Number of floors | 2
Building construction volume, m3 | 293500
Booster and Nuclotron
Cryogenic area
BM@N
Extracted beam
MPD
SPD

## Slide 4: Collider building #17 Ground floor
Water cooling area
One of the hallways with engineering communications on the ceiling and entrance gates
Collider tunnel
MPD hall
Ground floor parameters | 
Name | Unit, m2
Tunnel area | 5182
MPD hall | 1996,5
SPD Hall | 1996,5
Electron cooling | 106
Water cooling | 420
Power supply area | 450
Total control rooms (PS, MPD, SPD, EC…) | 180
Engineering equipment technical rooms | 395
Technical staff rooms | 450
Collider tunnel

## Slide 5: Collider building #17 First floor
First floor parameters | 
Name | Unit, m2
Electron cooling power area | 380
Water cooling | 210
Power supply area | 450
Office area, temporary collider control rooms | 220
Engineering equipment technical rooms | 5500
Technical staff rooms | 450
Civil works of the collider building is ready for technical run
Example of one of the hallways
Climate control system
Cooling system
Control and office rooms
Electrical power racks

## Slide 6: Engineering systems Cooling water system
Water cooling consumers
Electrical power of the collider
MPD detector and subdetectors
Cryogenic and vacuum systems
Electron cooling systems
SPD detector
Cooling system parameters |  |  |  | 
Index number of cooling center | 1 | 2 | 3 | 4
Cooling capacity | 1335 kW | 1540 kW | 1290 kW | 453 kW
Refrigerant | Antifreeze, still water, freon, purified water |  |  | 
Number of consumers | 10 | 10 | 9 | 2
Range of water temperature | 18 - 300C | 15 - 550C | 15 - 250C | 18 - 240C
Operation modes* | Dry cooling, cooling machine, mix mode |  |  | 
* depends on consumers
** depends on ambient temperature
Water cooling system including 4 similar cooling centers. Cooling center is complicated and uses 4 different coolants. Three operation options are available depending on the ambient temperature. This scheme allows obtaining stable temperature at the collider and detector equipment in the whole operation range regardless of the season.
For technical run of the collider, #1 and #2 cooling centers are required
Cooling centers are ready for operation by the local automatization system
Dry cooling

## Slide 7: Engineering systems Power electricity of NICA complex
Temporary scheme of the collider power supply for the technical run
29 Apator power racks and 56 Laboratory power racks were ordered for the operation of the collider power supply. Unfortunately, the delivery of racks from Apator has been delayed.
Developed temporary scheme of the collider power supply for the technical run involves the use of 19 Laboratory racks and 2 main power racks (300 kW and 237 kW electricity power).
Two temporary main power rack instead of 29 Apator
Collider power system parameters |  |  | 
Name | Total | Technical start | Notes
Apator power rack | 29 | 2 | Reorder in TES company (installed at JINR)
Laboratory power rack | 56 | 19 | Order in TES company (delivery 10/02/2025)
All power supply equipment for the collider technical run is ready, or has being delivered

## Slide 8: Engineering systems Automatization
Upgrade of cryogenic station
Visualization and control scheme of water and heat supply system on all VBLHEP area
A new automatization group was established at VBLHEP. The main task of the group is to automate or support technical process of the equipment, automate control and regulation of engineering system parameters on the collider building
*Drawings and information by A. Kolesnikov

## Slide 9: Cryogenic system of NICA complex Ready for the technical launch of the collider in 2025
Scheme of cryogenic NICA complex
Nuclotron
The main goal of the cryogenic department for 2025 is to ensure the cooling of all rings of the NICA complex, as well as the operation of liquid helium consumers (Cryon, MPD, magnet test stand).
Main cryogenic equipment of the
NICA complex
3 Satellite refrigerators (each cooling capacity is 2000 W at 4.5K);
2 Turbine refrigerators (each cooling capacity is 2000 W at 4.5K);
Liquefier (capacity of LHe is 1000 l/h)
Compressor complex;
Oil removal system for each of the compressor
Cryogenic LN2 and LHe pipes
Warm straight and return pipelines
*Drawings and information by A. Konstantinov

## Slide 10: Cryogenic system of NICA complex Ready for the technical launch of the collider in 2025
Satellite refrigerators in the collider building
- To cool the collider, 2 satellite helium refrigerators #2, 3 were installed in room 177 of collider building #17.
- In December 2024, they were successfully launched with cooling to the temperature of liquid helium.
- The cooling capacity of each unit is 2000 W at 4.5 K.
- In January, the refrigeration control circuits will be adjusted.
SR are being tuned now and will be ready
by 01/02/2025
Liquefier 1000 and compressor complex
- Liquefier 1000 successfully operated at the MPD detector cooling during the run, filling 12 m3 of tank containers with liquid helium.
- The staff of the cryogenic department optimized the starting modes of the liquefier, which reduced the cooling time of the tanks and reduced energy costs.
- Liquefier has confirmed the design capacity of 1000 l/h of liquid helium.
- Two new compressors “Kaskad -110/30” successfully operated during the MPD cooling session.
Liquefier 1000 and compressor complex
are ready for the run from 01/02/2025
Cryogenic LHe, LN2, warm straight and return pipelines
LHe
LN2
- Warm pipe is ready and tested.
- LN2 pipes are progressing as planned and will be finished in January 2025.
- LHe pipe in the west side will be ready on 15/02/2025.
- LHe pipe in the east side will be ready on 30/03/2025
*Drawings and information by A. Konstantinov

## Slide 11: MPD detector engineering system and cooling status
Screen of the temperature at the solenoid
- In December 2024, cooling of the MPD solenoid was performed to an operating temperature of 4.5K.
- The cooling lasted 15 days to nitrogen temperature and 6 days to operating temperature.
- No cold helium and nitrogen leaks were detected.
- Operating temperature was maintained for 15 days.
- Resources parameters of cooling and operation modes correspond to the designed.
- Preparation of power supplies and quench detector test.
- Cryogenic system (complete without main LHe pipe, delay until march).
- Power supply system (connected, started test in the December 2024).
- Quench and protection system (started test in the end of January).
- Water cooling system (ready).
- Magnetic field measurement equipment should be installed inside solenoid from 24/02/2025.
Main engineering equipment

## Slide 12: MPD detector engineering system and cooling status
Control and electricity power scheme of MPD magnet
Water cooling system
Screen of the control panel water system
Controlled parameters
Temperature of TRIM coils 25-550С
Flow rate of TRIM coils
TRIM1 – 1076 l/h
TRIM2 – 2210 l/h
Flow rate of Power supplies
PSTRIM1, PSTRIM2 – 720 l/h
SCPS – 1800 l/h
In December 2024, testing of the solenoid power supply from the local control software began.
All warning and alarm signals were detected and removed.
Output current was 100 A, and the rise rate can be tuned (during the test it was 1A/sec).

## Slide 13: Main power station GGP1
Upgrade of the GPP 1 was the twofold increase in electricity power.
From 22396 kV (40 MW) to 40800 kV (80 MW).
Out of the 40800 kV, 34300 kV for JINR and 6500 - for Dubna city.
The final successful commission from Rostechnadzor was carried out in the December 2024.
Permission
for admission to the operation of a power receiving unit

## Slide 14: Development of VBLHEP area
The development of the new checkpoint is ongoing.
Development includes new transport ways.
In 2024, two parking areas with 400 spaces were constructed.
The traffic reorganization is expected to start in May - July 2025

## Slide 15: Conclusions
Two important licences were obtained in 2024.
Admission of main power station explanation (GPP1)
License for the construction of radiation sources
Collider building is ready for technical launch of the collider.
Building facade…………………………………………….100%
Earthmoving work, pile,
concrete, walls, etc……….…………………………………….100%
Roofing work……………………………………………….99,9%
Interior finishing work…………………………………….99,9%
Technical engineering infrastructure of collider (expected to be ready for 2025 run)
Water cooling center # 1, 2 - ready for operation in manual modes
Power supply of the collider is expected to be ready for the start of the technical run under a temporary scheme
Equipment of cryogenic complex (refrigerators, compressors) is ready for the collider run. Completion of mounting of the cryogenic pipeline in the west side until 15/02/2025, the east side - until 30/03/2025
MPD detector was successfully cooled to operating temperature in December 2024. Work is now continuing on the power supply and protection system. Magnetic field measurements are expected to begin in March.
Development of the VBLHEP area
Work is scheduled to start in May - July to reorganize the transport scheme at the VBLHEP entrance gate.

## Slide 16: Thank you for attention