## Slide 1: Status of the solenoid start-up
Speaker: K. Mukhin
JINR, LHEP 2025
NICA Days and XV Collaboration Meeting of the MPD Experiment at NICA
15-17/04/2025
From drawing
to detector

## Slide 2: Plan of talk
Magnet construction and some parameters
Cryogenic infrastructure
- Cooling to operation temperature (4,5K)
Engineering systems of the detector MPD
- Power supply system
- SC coil training
- Water cooling system
- Magnetic field mapper
and stationary gauges
Timeline and risks

## Slide 3: Chapter 1 Magnet construction and parameters

## Slide 4: MPD in NICA complex
SPD
BM@N
Booster
Nuclotron
N I C A
MPD

## Slide 5: MPD magnet construction
Parameters of the magnet | 
Magnetic field | 0,57 T
Cryostat weight and size (diameter/length) mm | 66 tons 5443/7910
Yoke weight and size (diameter/length) mm | 630 tons 6583/8970
Current Voltage | 1790 A 10V
Each pole weight | 45 tons
Total weight with support equipment | 800 tons

## Slide 6: Superconductor cable
Original SC cables for MPD
Winding and tests of SC cable in ASG
SC cables parameters
SC Materials – NbTi/Cu.
Cable composition is pure aluminum matrix (4,1 x 20 mm) and inside string of Cu/SC ratio 0,9/1 (d – 1,5 mm).
Insulation – kapton tape, glass tape and epoxy resin.
Critical current (1,2 T, 4,5 K) – 6,9 kA
Cable length - 27 km.
Cable weight – 6,3 tons
LHC 27 km

## Slide 7: Chapter 2 Cryogenic infrastructure. Cooling to operation temperature (4,5K)

## Slide 8: Cryogenic infrastructure
Control Dewar
Refrigerator
NTCS (Nitrogen temperature correction system)
LN2 and LHe heaters
LHe pipe
Cryogenic flexible connection pipes
LN2 Tanks (2 pc)
LHe Tanks (2 pc)
LN2 transfer pipe 120 m
Warm pipes for He, N2 and instrumentation Air
Flexible warm pipes
Support system for flexible pipes
Temporary pipes for cooling by temporary scheme

## Slide 9: Scheme of cooling down to 4,5 K

## Slide 10: Cooling process scheduled
Total cooling time – 28 days
Nitrogen mode – 14 days
Transient mode – 6 days
Helium mode – 8 days

## Slide 11: Conclusions of cooling to 4,5K
Successful cooling solenoid by 4,5 K.
No cold leak in thermal shield and LHe circle.
Obtained cooling parameters of cryogenic equipment can be accept and are consistent with a manual (1 - 1,5K/h).
Heat load into solenoid are consistent by project and low then 100 W.
Cooling time from room temperature to 80 K take’s about 15 days, from 80 K to 4,5K 8 days.
Main LHe pipe was developed and installed in to MPD Hall
From the March 2025 for present day solenoid MPD operation temperature (4.5K) for power supply tests.

## Slide 12: Chapter 3 Engineering system of the detector MPD
Engineering systems of the detector MPD
- Power supply system
- SC coil training
- Water cooling system
- Magnetic field mapper
and stationary gauges

## Slide 13: Power supply system

## Slide 14: SC power supply test and the first current in to SC coil
SCPS test to 500A in CS coil and emergency stop
Emergency stop
Voltage drop
Test scheme
Inductance of coil – 8,6 H
Nominal current – 1760 A
Number of turns – 1674
Magnetic field – 0,57 T

## Slide 15: SC coil training
0
100A
200A
300A
400A
500A
600A
700A
750A
0,221 T
0,135 T
0,16 T
0,188 T
0,107 T

## Slide 16: Factory test of power supplies
Power supply of solenoid I = 2500A V= 10V
Power supply of TRIM1
I = 3000A V= 70V
Power supply of TRIM2
I = 1300A V= 45V
140
53

## Slide 17: Water cooling system
Cooled equipment
TRIM COIL 1
1076 l/h water in 250C out 550C
TRIM COIL 2
2210 l/h water in 250C out 550C
POWER SUPPLY of SOLENOID
1800 l/h water in 250C out 350C
POWER SUPPLY of TRIM 1
720 l/h water in 250C out 350C
POWER SUPPLY of TRIM2
720 l/h water in 250C out 350C

## Slide 18: Cold water system scheme
Controlled parameters
Temperature of TRIM coils
Flow rate of TRIM coils
Flow rate of Power supplies

## Slide 19: Colling water system of NICA complex
Water cooling consumers
Electrical power of the collider
MPD detector and subdetectors
Cryogenic and vacuum systems
Electron cooling systems
SPD detector
Cooling system parameters |  |  |  | 
Index number of cooling center | 1 | 2 | 3 | 4
Cooling capacity | 1335 kW | 1540 kW | 1290 kW | 453 kW
Refrigerant | Antifreeze, still water, freon, purified water |  |  | 
Number of consumers | 10 | 10 | 9 | 2
Range of water temperature | 18 - 300C | 15 - 550C | 15 - 250C | 18 - 240C
Operation modes* | Dry cooling, cooling machine, mix mode |  |  | 
* depends on consumers
** depends on ambient temperature
Water cooling system including 4 similar cooling centers. Cooling center is complicated and uses 4 different coolants. Three operation options are available depending on the ambient temperature. This scheme allows obtaining stable temperature at the collider and detector equipment in the whole operation range regardless of the season.
Dry cooling

## Slide 20: Magnetic field measuring and control
Volume field mapper measuring device
Calculation and experimental current for optimal field configuration
*Drawing of mapper by S. Gerasimov
*Computing calculation table data by E. Antokhin

## Slide 21: Stationary magnetic field monitor
40 – sensors evenly distributed over the inner surface of the solenoid.
36 – sensors (16 on 200 mm. from end face of solenoid and 4 in the center)

## Slide 22: Timeline and risk
February 2025 – present day – Solenoid at temperature 4,5 K
April – May 2025 – The training of a superconducting coil involves the input of current up to 1000 A for a short time (300-500 A for several days). Tests of quench protaction system and storage energy evacuation on low current.
Until end of April 2025 – Finalizing mechanical and magnetic test of a mapper in INP
Until May 20th – Shipment all components of a magnetic field mapper from INP (Novosibirsk) to JINR and start assembling it in the solenoid.
May 2025 – Starting measuring of the magnetic field from 1000 Gs including determination of magnetic axis and coil position depends of current.
May – June 2025 – Magnetic field measurement.
Further increase in current is impossible without cooling the water.
Checking the operability of current leads at high current (electrical connections and thermal contact). At currents over 500 A, the temperature of the SC cables increases

## Slide 23: Thank you for attention