## Slide 1: State of MPD DCS and plans for 2025
State 2025.04
S.Sergeev

## Slide 2: MPD DCS structure
FFD DCS
TPC DCS
DAQ
TOF DCS
ECAL DCS
LV
HV
Laser
…………
Cooling
…………
Shift leader
Predefined set of RUN types
RC/CDCS
Server
HW
Client
Client
Client
Client
Diagnostics tools
Command
State
Config DB
Client
Command –> set run type
State – actual subdetector state
Off, StdBy, NotRdy,
Rdy, Wrng, Error,…
Run type DB

## Slide 3: Interfaces actual state
Agreed with subdetector teams and tested
Solenoid -> MS4D -> DIM -> CDCS
DAQ -> DIM -> CDCS
ITS -> WINCC OA -> DIM -> CDCS
TPC -> MS4D -> DIM -> CDCS
FFD -> home-made hw/sw -> DIM -> CDCS
ECAL -> Tango -> DIM -> CDCS
TOF-> Tango -> DIM -> CDCS
fHCAL -> DIM -> CDCS
Lumi -> Tango -> DIM -> CDCS

## Slide 4: DCS framework
Central DCS application – prototype runs
Subdetector root node - prototype runs
  Has GUI
  Adjustable for subdetector architecture
  Joins Linux and Windows computers
Converter local files <->DIM – final version runs
Hardware Server Emulator – runs
DIMTree - DIM address space browser (runs at Windows and Linux)
Started TPC integration. During this process the Root node application to be modified

## Slide 5: TPC DCS
CAEN
HV
IV
HV
TPC DCS Root Node
CAEN
CAEN
LVDB
LV
Custom
Custom
Custom
MasterScada 4D
PostGre SQL
OPC UA
DIM
CDCS/RC
Interface MasterScada_4D <-> DIM ready
Windows
Windows
Linux
Linux
Windows
Cooling
Gas
Laser
In progress

## Slide 6: CDCS manager I

## Slide 7: CDCS manager II

## Slide 8: SubDetector Root Node I
Receives states of subdetector subsystems using DIM Info Services
Builds resulting subdetector state
Receives commands from CDCS.
Parses CDCS commands and converts to subdetector subsystems commands.
Sends commands to subdetector subsystems using DIM Command Services
GUI for configuration command editing
Adjustable for MPD subdetectors

## Slide 9: Root Node, DIM item selector

## Slide 10: Root Node, Command selector

## Slide 11: Root Node, Test run

## Slide 12: Disk file to DIM Converter
Reads local files containing subsystem state with refresh period ~1 sec. Converts content of file to DIM Info item
Checks “heart beat” and generates OFF state if no data refresh occurred during predefined time
Receives DIM commands from subdetector Root Node and records command content to a disk file
One file – one DIM item
One subdetector could run Converter copies at different computers
To be ready in mid-November for Windows and by the end for Linux

## Slide 13: Safety issues
Each DIM command contains a process ID and a name of a computer issued the command (Command Source ID, CSID)
Root node has a possibility to create a list of trusted hosts which could send a command
Each command service should check a CSID of a command
The CDCS publishes its CSID and root nodes could get it in a real time mode
The Root Node also publishes its CSID and hardware servers also could get it in a real time mode
DIM protocol does not allow to have two items with the same name in a common name address space so there is no simple way to send a command by mistake

## Slide 14: Plans for 2025
TPC integration
Other subdetectors?
Migration of CDCS manager to Linux
Modification of the RootNode application for Linux (to have common version for both Windows and Linux)

## Slide 15: Thank you
State 2024.10.01

## Slide 16: DCS emulator

## Slide 17: CDCS interface I
RC/CDCS subscribes to published by subdetectors state InfoItems with names
  MPD_DCS_State/<subdetector name>
Run configuration contains subdetectors list used in a run
RC/CDCS sends run type name (text) to all CommandItems of subdetectors being in a list. CommandItems should have a name like
  MPD_DCS_IniCmd /<Subdetector name>
Draft 2024.05.10

## Slide 18: CDCS interface II
Each subdetector DCS root node could (should?) have a CommandItem with name
  MPD_DCS_DisplayCmd/<subdetector node name>
  A command received by this CommandItem should start diagnostic tool (see below)
DAQ should have additional Info/Command items to provide vital information to/from the RC/CDCS (to be discussed with DAQ team)
Draft 2024.05.10

## Slide 19: CDCS interface III
RC/CDCS has a CommandItem MPD_DCS_Messages to receive messages from subsystems/subdetectors
Format of message should be like (to be discussed)
  <subdetector name>_<severity level>_<message text>
    <severity level> defines a way to process the message
      0 -> just to show in a window. Could be scrolled by messages arriving later
      1 -> stays at the screen until confirmed
      2 -> stays at the screen until confirmed + sound alarm if not confirmed during defined time (1 min as an example)
      3 -> stays at the screen until confirmed + instant sound alarm
All messages have a text content
Draft 2024.05.10

## Slide 20: States and colors
  State=-1, Item does not have a state, no color to be displayed
  State=0, OFF - any of sub-elements does not respond
  State=1, StdBy – any of sub-elements is in stand-by mode
  State=2, NotRdy – any of element is in transition state (Time-out should be implemented)
  State=3, Ready – all elements are OK
  State=4, Wrng – any of elements is in Warning state
  State=5, Error – any of elements is in Error state
  State=6, Ignrd – node in Partitioned state
Draft 2024.05.10

## Slide 21: Extended display (to be discussed)
  A subdetector should provide a set of diagnostics tools stated by a CommandItem
  MPD_DCS_DisplayCmd/<subdetector name>
This should be an application running at a CDCS PC or a web-page running AJAX script (?). The web server could be provided by a CDCS. Page content should be developed by the subdetector team and could be located at a common disk space
Start parameters are defined in the CommandItem command content
Draft 2024.05.10

## Slide 22: Extra parameters interface
“MPD_DCS_State/DAQ”, content=“3”
“MPD_DCS_State/DAQ/Subsystem1”,
content=“3_value=XXX”
“MPD_DCS_State/DAQ/Subsystem1/Value1”,
content=“3_XXXXX”
“MPD_DCS_State/FFD/Laser_power”,
content=“-1”
“MPD_DCS_State/FFD/Laser_power/”,
content=“-1_80%”
Extra info to display in the tree, defined by subsystem/subdetector
Obligatory
Draft 2024.05.10
MPD state is built using 1-st level nodes