## Slide 1
Distributed control system for the BM@N experiment
I. Osokin
on behalf of Slow Control group:
V. Dronik, V. Shutov, R. Nagdasev, D. Egorov
Alushta-2025
10.06.2025

## Slide 2: BM@N Experiment
BM@N building in NICA complex
BM@N experiential hall:

## Slide 3: BM@N subsystems

## Slide 4: What is Slow Control?
Monitoring of the experimental hardware;
Centralized control of the Slow Control equipment (LV, HV, gas flow etc.);
Archiving historical Slow Control data;
Alarm system.
Not a Slow Control:
Main data stream (data taking);
Event builder (reconstruction)/event display;
Data quality;
Run control.

## Slide 5: What is Slow Control?
What and how read from server?
Data and command exchange
Monitoring and controls for users
Tango-based Slow Control System has performed well in previous runs and will be used in the forthcoming run
DCS analogs:

## Slide 6: Infrastructure – computing, devices, interfaces
At present time the service layer tasks uses existing MPD/BM@N computing farm. Virtualization is done using PROXMOX Virtual Environment.
All centralized services are running on dedicated VM’s
Front-end layer includes a wide variety of devices which are uses different buses and protocols, such as PXI, Ethernet, RS-485, RS232 etc.

## Slide 7: Database cluster

## Slide 8: Data visualization
Grafana is a free software data visualization system focused on IT monitoring systems data. It is implemented as a "dashboard" style web application with charts, graphs, tables, alerts.

## Slide 9: HV system of FSD, GEM, BT
Historical
DataBase
TCP/IP
TANGO device server

## Slide 10: HV system of FSD, GEM, BT
The change in detector currents at three beam tracker stations during the 2022-2023 session is shown.
The average value
of the dark current at the beginning of the session is 0.761 µA, measured at a temperature of
+22.5°C; the average value of the dark current at the end of the session, for a reason radiation damage, is 12.7 µA,

## Slide 11: LV system of FSD, GEM, BT
Historical
DataBase
TCP/IP
TANGO device server

## Slide 12: FSD FEE temperature
HDB
TCP/IP
TCP/IP

## Slide 13: FSD Autoswitch system
Temperature heating over 80˚C
Increasing dark currents of silicon detectors

## Slide 14: FSD Autoswitch system
Temperature threshold
Delayed automatic
LV shutdown

## Slide 15: FSD Autoswitch system
Temperature threshold
Delayed automatic
LV shutdown

## Slide 16: FSD Conditioner monitoring
Historical
DataBase
TCP/IP
MAI6 & WB M1W2 Measurement modules
Modbus RTU
TANGO device server

## Slide 17: Conclusions
Thank You for attention!

## Slide 18
FSD – Forward Silicon Detector
63
63
126
FEE board
7/12
Coordinate plane from double side Si-modules
n+ side
p+ side
639
0
0
639
Pitch Adapter (n+) side
Number of channels: 640 Value of poly-Si resistors: ≈ 1 MΩ
Value of integrated capacitors: ≈ 120 pF Capacitor working voltage: 100 V Capacitor breakdown voltage: >150 V Manufactured by ZNTC (Zelenograd)
ASIC VATAGP7.2 (5 chips on each side of module)
Number of CSA: 128 channels Dynamic range: ±30 fC
Peaking time (slow/fast shaper): 500 ns/ 50ns Noise (ENC): 70e +12e/pF (typ.) Voltage supply: +1,5 V, -2,0 V
Gain from input to output buffer: 16,5 µA/fC Output Serial analog multiplexer clock speed: 3,9 MHz
Power dissipation per channel: 2,2 mW
Notes: (сделать обозначения и показать стрелками)

## Slide 19: SiBT – Silicon Beam Tracker
SiBT 1
SiBT 3
SiBT 2
SiBT 1
SiBT 2
SiBT 3
16/20