## Slide 1: BM@N SLOW CONTROL SYSTEM
D. Egorov
V. Shutov P. Сhumakov R. Nagdasev

## Slide 2: What is slow control
Monitoring of the experimental hardware
Centralized control of the Slow Control equipment (LV, HV, gas flow etc.)
Archiving Slow Control data
Alarm system
SC Configuration database
Is not Slow Control:
Main data stream (data acquisition)
Event builder (reconstruction)/event display
Data quality
Run control

## Slide 3: Main goals of sc system
Centralized control of diverse hardware
Scalability
Reliability – monitoring of hardware and software operation
Easy incorporation of existing subsystems and new hardware
Storage of Slow Control data in unified format
Common Slow Control configuration database for all subdetectors (HV, thresholds etc. )
Access control
Modern and easily customizable user interface

## Slide 4: Options for bmn sc backbone
 | Tango Controls | EPICS | WinCC (PVSS)
Free | + | + | -
Open-source | + | + | -
Crossplatform | + | + | -
Multiple language and commercial system bindings | + | + | -
Scalability | + | ± | +

## Slide 5: Detailed view on tango CS
TANGO control system is a free open source device-oriented controls toolkit (middleware) for building SCADA systems.
Multiplatform
Code generator for C++, Java, Python
Archiving service
Commercial bindings (Labview, Matlab …)
GUI Toolkit for Java, QT, Python
Access control service
Logging service
Alarm service
Configuration tool
Administration tool
Web interface

## Slide 6: BMN at 55th nuclotron run
About 1 month of data taking
Slow Control system archived > 30 Gb of data
Smooth and proper work with minimal human interaction
Simple and useful alarm system

## Slide 7: Baryonic matter at nuclotron experiment

## Slide 8: Status monitoring of bmn subsystems
Desktop application, that displays status of all subdetectors’ equipment, which is controlled by SCS. The color of detector show hardware state according to its priority (OFF>ALARM>WARNING>ON).
Also value from hall sensor and information from DAQ system are presented in the application window.

## Slide 9: MWPC and tof400 hv
Both detectors are using Wiener MPOD power supplies. All data from crate can be obtained by SNMP.

## Slide 10: Trigger unit monitoring
Due to subdetector policy and their hardware complexity, SCS does not have direct access to devices.
All required data is sent in JSON format (which is standard for data exchange in BMN SCS) through TCP-socket server, and handled by our JSON Parsing Tango server, which converts received data to Tango attributes.

## Slide 11: Magnet field monitoring
Hall sensor measurements are read by ADC, implemented in BMN SCS.

## Slide 12: gem, dch and si tracker HIGH VOLtage and low voltage
These detectors are using the same high voltage and low voltage hardware, made by Wiener, and software, that is written in Labview.
Tango has bindings for Labview, so it’s easily implemented into existing Slow Control System.

## Slide 13: Tof400 and tof700 hv
Both detectors are using HVSys high voltage modules, with existing software.
Implemented TCP-socket server send information on request about module to Tango JSON Parsing server.

## Slide 14: Tof400 gas control
Gas control application is used to control and monitor gas flow of system based on MKS PAC-100 modules;
Scales made by CAS with RS-232 interface is using for weight measurement of gas containers for TOF detectors;
Oxygen and humidity sensors made by GE Measurement are used to control the quality of gas mixture.

## Slide 15: Tof400 gas control

## Slide 16: Tof400 preamplifier control and monitoring
This application monitors preamplifiers’ parameters, like power voltage, thresholds, temperature, and can control its’ DAC.
X 20

## Slide 17: Ecal and zdc hv
Both detectors are using HVSys high voltage modules, with existing software.
Implemented TCP-socket server send information on request about module to Tango JSON Parsing server.

## Slide 18: Network switch monitoring
Poe switch control the client application to control power over Ethernet (PoE) on a switch (particularly HP J9574A).
Monitors power and network status on each port;
Lets user enable, disable and reset power and network connection of selected switch ports;
Supports multiple devices.

## Slide 19: DAQ VME crate control
Crate Control is a desktop application that was developed for monitoring and control of crates made by Wiener and ELMA companies.
Main functions:
Switch on/off one crate, or all at once
Reset
Monitor state and detailed status of crates
…

## Slide 20: Uninterruptible power supply monitoring
Uninterruptable power supplies application shows information about power sources at BM@N:
Input and output voltage
Load
Battery info and remaining time
Additional info and load by port

## Slide 21: Conclusion
The system so far successfully worked during 4 Nuclotron runs;
Almost all subdetectors’ groups are involved in work and their devices are implemented in BMN Slow Control System;
User notification system can be improved and more devices added;
Existing BMN Slow Control System will be base for the future MPD Slow Control System.

## Slide 22
THANK YOU FOR
ATTENTION

## Slide 23: BMN sc system layout
PCs
VMs
Tango middleware
PCs
Front-end layer
Service layer - VMs (Linux)
Client layer – PСs (Linux, Windows)
Ethernet – serial bus convertors(RS485, RS232 …)
devices
devices
devices
Central Services:
- Tango DB
- Configuration DB
- Archiving
- ……
storage
Applications
Device servers

## Slide 24: Example of diverse hardware
Multiple firms: WIENER, CAEN, HVSys
Hardware controlled by the software with ideologically different approaches: OPC server, LabVIEW, standalone programs
Protocols: SNMP, OPC XML-DA, proprietary.

## Slide 25: Tango graph
Can handle multiple graphs, independent from each other, with different timescales, polling period and many other options
Loadable attribute pre-history from database to display directly on graph
Completely configurable with a single .ini file
Space saving
Every section has it’s instruments for view manipulation, such as pan-view and zoom
Any point of data can be annotated and tracked
Provides section view export in common formats like PDF, SVG.